COM465IP Condition Monitor with an integrated Ethernet gateway for the connection of devices with the Bender protocols BCOM/BMS and Modbus RTU/TCP to networks using the TCP/IP protocol family.
 
The Condition Monitor supports commissioning and diagnosis of BMS and BCOM systems, and allows observing and analysing communication-capable Bender products, such as universal measuring devices, RCMS, EDS and MEDICS systems. The Condition Monitor is integrated in the existing EDP structure like a PC. After connection to the bus systems, all assigned devices can be accessed from any personal computer using a standard web browser (e.g. Google Chrome, Internet Explorer etc.). 
The language displayed on the web browser is adjustable (DE/EN/ES/FR/IT/DA/HR/KO/PT/SLO/SR/TR/CS/NO...). A total of 25 languages are available.
 
Bender systems can be integrated into SCADA (Supervisory Control and Data Acquisition) systems via the integrated Modbus TCP server.

Features:
- Optimum presentation of current operating/alarm messages and measured values from Bender devices and/or universal measuring devices on a personal computer via a standard web browser
- Help function to display additional information about messages and alarms, in part with instructions for further action
- Diagnosis functions for BMS/BCOM systems
- Integration of third-party devices or Bender devices (PEMxxx, energy meters) via Modbus RTU/TCP
- Remote access and remote diagnosis via LAN, WLAN or Internet
- Ethernet 10/100/1000 Mbit (RJ45)
- Time synchronisation for all Bender BMS/BCOM and Modbus devices (time master, SNTP)
- Multi-level password protection

Additional functions in function modules can be used and combined independently:
 
Function module A – 'Individual messages'
- Individual descriptive texts can be added to each device and each measuring point
- Customized system overview through individual system description
- Selective e-mail notifications to be sent in the event of an alarm or system fault to different groups of users, with TLS/SSL support
- History memory to record alarms and tests that have been carried out with a timestamp for start, acknowledgement and end of the alarm and including entries for minimum and maximum measured values
- Data loggers for optional recording and storing of measured values
- History memory and data loggers can be read out over the menu
- Create documentation as PDF for settings/parameters, history memory and data loggers
- Devices can be monitored for failure

Function module B - 'Modbus TCP gateway'
- All alarms, status messages and measured values of all assigned devices are made available by the integrated Modbus TCP server. This allows the use of professional 
visualisation programs or coupling to PLC.
- Reading out alarm and measured values via SNMP protocol (V1, V2c or V3)

Function module C - 'Parameter setting'
- Setting of all device parameters of the devices in the system via a web browser
- Saving and restoring device settings by means of the backup function

Function module D - 'Visualisation'
- Integrated browser-based visualisation for the Bender system
- System display on different pages
- Any required background images can be used
- No programming skills required for configuration

Function module E - 'Virtual devices'
- Integration of 100 virtual devices with 16 channels each

Function module F - 'Integrating third-party devices'
- Integration of 1,600 data points from third-party devices 

Supply voltage: 	AC/DC 20...240 V or
				DC 24 V

Indicators: LEDs (Power, ETHERNET/IP, MODBUS RTU, BMS)

Interfaces:      		
RS-485: BMS, Modbus RTU 
Ethernet: BCOM, Modbus TCP

Ethernet adapter: RJ45, 10/100 Mbit/s
IP address: adjustable via menu or DHCP

Transmission rates: 
Internal BMS bus: 9.6 kbit/s
External BMS bus: 19.2...57.6 kbit/s
Modbus RTU: 9.6...57.6 kbit/s

Terminating resistor integrated, switchable

Operating modes:
BMS master (with address 1) 
BMS slave (with address 2-99)

The enclosure is suitable for:
- Installation into standard distribution panels acc. to DIN 43871
- DIN rail mounting acc. to DIN EN 60715
- Screw mounting

Scope of delivery:
- Delivery of COM465IP
- 1 x terminal for power supply
- 1 x terminal for interfaces (BMS, Modbus RTU)
- Short operating instructions
- Operating manual included in the device (readable via any browser)
- Safety information

Manufacturer: 	
Bender GmbH & Co. KG
Londorfer Str. 65   
35305 Grünberg

Type: COM465IP (function can be expanded with function modules A, B, C, D, E and F)